## Sheet1
LP1050D Series
50W single output LED display Din-rail power supply
Features: 1.Protection charateristic:short circuit/overload/overvoltage 2.High efficiency,hihg reliability and long serive life. 3.Natural air cooling 4.100% full load burning test 5.LED power indication
Model / Specification |  | LP-50-5 | LP-50D-12 | LP-50-24
Output | DC Output Voltage | 5V | 12V | 24V
| Output Voltage tolerance | ± 2% | ± 1% | ± 1%
| Rated Output Current | 8A | 4.2A | 2.1A
| Output Current Range | 0-8A | 0-4.2A | 0-2.1A
| DC Output Power | 40W | 50.4W | 50.4W
| Tripple and Noise | 80mVp-p | 120mVp-p | 240mVp-p
| Adjustable Range for DC Voltage | 4.75-5.5V | 11.4-13.2V | 20.5-26.5V
Input | AC Input Voltage Range | 90-264VAC or 100-360VDC 47~63Hz;
| AC input current | 0.9A/115VAC 0.45A/230VAC
| Efficiency | 78% | 83% | 85%
| AC Inrush Current | Cold-Start Current: 18A/115V, 36A/230V
| Leakage Current | <2mA/240VAC
Protection charateristic | Overload Protection | 110%-150%
Protection mode: cut off output and restart
| Over Voltage Protection | 5.75-6.75V | 13.8-16.2V | 27-30V
Protection mode: cut off output and reset automatically
Environment | Work Temperature Humidity | -10℃~+50℃ , 20%~90%RH
| Storage Temperature Humidity | `-20℃~+85℃, 10%~95%RH
| Shock resistance | 10~500Hz, 2G 10min,/1cycle,duration:60min each shaft
Safety | Voltage withstand capacity | Input-output:2KVAC Input-earth:1.5KVAC Output-earth:0.5KVAC
| Insulation resistance | Input-output, Input-earth ,Output-earth:100M Ohms/500VDC
Executive Stantand | Safety Standards | CE
| EMC Standards | Design refer to FCC part 15J Conduction Class B
Others | Weight | 0.22KGS
| Package | 60pcs/ctn 38.5*32*28
| size | 75.5*45*102(L*W*H)
Notes | 1. All parameters except special situtation, are meaured under 230VAC voltage input and rated load at 25℃. 2. The ripple and noise voltage are measured in condition capacitance of 0.1μ and 47μ are applied to ends of 12inch twisted-pair of 20MHZ bandwidth oscilloscope. 3.The tolerance is the sum of setting voltage error , voltage and current regulation factor.