EMAS ELEKTROTEKNİK MAKİNA    SANAYİ VE TİCARET A.Ş

Ziya Gökalp Mah. İkitelli Organize Sanayi Bölgesi Atatürk Bulvarı No:50 34490 Başakşehir / İstanbul / TÜRKİYE

Telefon : +90 212 549 22 52

Faks      : +90 212 549 25 80

Web      : www.emasas.com.tr

Technical Specification : PSA040AK441E

Order Code :

PSA040AK441E

-4 poles, on-off cam switches.

Contact and Assembly Schema :

Body :

General Specification:

General Specification :

Electrical Informations  :

Standards :

-TS EN 60947-3

-High precision

-Long life time

-High contact reliability

-Compact design

-Handle designed in comformity with finger ergonomy

| -Operating Temparature | -5 / +40 °C |
| --- | --- |
| -Mechnical Life | 100.000 (900 op/hour) |
| -Electrical Life | 50.000 (450 op/hour) |
| -Protection Degree | IP20 outside board IP54 inside board IP65 inside box |

| -Range of use |  | AC1 / AC21 |
| --- | --- | --- |
| -Operating Voltage | Ue | 400 V |
| - Fregquency |  | 50 Hz |
| -Termal current | Ith | 50A |
| - Operating Current | Ie | 40A |
| - Insulation voltage | Ui | 690 V |
| - Stroke resistance voltage | Uimp | 4 kV |
| - Short circuit breaking capacity | Icn | 6 kA |
| - Insulation Resistance |  | min 10MΩ |

Technical Information :